ChargePoint Guide Specification

Notes and instructions to Specwriter

The following guide specification is offered for your assistance in specifying this product as part of a CSI (Construction Specification Institute) compliant document. This guide specification has been created in MS Word and uses Word features including Styles and Review to assist in editing and formatting.   You may also find it helpful to view the document in Outline mode when editing or selecting sections to copy/paste into your base document.

Styles

Styles are provided for all paragraph types described in the CSI Masterformat.  Applying a Style to text will provide the correct indentation, paragraph letter/number, font, capitalization, etc.  Styles are shown on the right-hand side of the Word “Home” ribbon.

Review

“Notes to Specwriter” (when available) are provided using the Reviews feature in Word.  To view “Notes to Specwriter” select “All Markup” in the Tracking dropdown menu on the Review ribbon.  To hide notes, select “No Markup”.   You can advance from one note to the next using the Previous and Next buttons on the same ribbon.  In earlier versions of MSWord hide notes by un-checking ‘Comments’ under Review>Show notes.  All comments should be deleted before printing or copying.

In cases where a selection needs to be made by the specwriter, valid options are shown in blue between brackets ( << >> ). The specwriter shall make the appropriate selection for the project and delete the other options. ChargePoint’s recommendations are shown in bold text.

Outline view

The Outline view within Word is often helpful when editing or copying sections from this Guide Specification.  Also, when pasting sections from this document into a base document, the specwriter may want to consider using right-click and “Merge Formatting’ or ‘Keep Text Only” features.

# Section 11 11 36.13

# level 3 DC electric vehicle supply equipment

# general

## References

### The ChargePoint charging stations shall be designed, manufactured and tested in accordance with the latest applicable standards of UL and SAE:

#### UL 1998 – Standard for Software in Programmable Components

#### UL 2251 – Standard for Plugs, Receptacles, and Couplers for Electric Vehicles

#### FCC Part 15 – Radio Frequency Devices

#### OCPP 2.0.1 – Open Charge Point Protocol, version 2.0.1

#### NFPA 70 (NEC) Article 625 – Electric Vehicle Power Transfer System

#### Energy Star Certified

#### FedRAMP LI-SaaS – Federal Risk and Authorization Management Program of the United States for Software as A Service

#### AICPA SOC 2 – Standard Control at a Service Organization Relevant to Security, Availability, Processing, Integrity, Confidentiality, or Privacy

#### ADA Standards – 2010 ADA Standards for Accessible Design; 2010

#### NTEP – National Type Evaluation Program to certify weights and measures

#### ISO/IEC 9001 - Quality management systems — Requirements is a document of approximately 30 pages available from the national standards organization in each country.

#### ISO/IEC 14443 – Standard for Identification Cards, Contactless Integrated Circuit Cards, Proximity Cards

#### ISO/IEC 15693 – Standard for Vicinity Cards

#### ISO/IEC 15118 – Standard Defining Vehicle-to-Grid Communication, Plug-and-Charge, Secure Communication, Smart Charging and other features

#### ISO/IEC 27001 – Standard to manage information security, cybersecurity and privacy protection

#### ISO/IEC 6100-4-5 – Standard to test surge immunity; 2017

#### IEEE 519 – Standard for harmonic control in electric power systems; 2022

#### NEMA 250 – Enclosures for Electrical Equipment (1000 Volts Maximum); 2020

#### SAE J1772 – SAE Electric Vehicle and Plug-in Hybrid Electric Vehicle Conductive Charge Coupler; 2017

#### CCS1 – SAE J1772 Combo 1 connector, or Combined Charging System

#### SAE J3400 – SAE Electric Vehicle and Plug-in Hybrid Electric Vehicle Conductive Charge Coupler, 2023, also known as North American Charging Standard (NACS)

#### UL 50E – Enclosures for Electrical Equipment, Environmental Considerations; Current Edition, Including All Revisions.

#### UL 2202 – Standard for Electric Vehicle (EV) Charging System Equipment; Current Edition, Including All Revisions

#### UL 2231-1 – Standard for Safety for Personal Protection Systems for Electric Vehicle (EV) Supply Circuits: General Requirements; Current Edition, Including All Revisions

#### UL 2231-2 – Standard for Safety for Personal Protection Systems for Electric Vehicle (EV) Supply Circuits: Particular Requirements for Protection Devices for Use in Charging Systems; Current Edition, Including All Revisions

#### UL 2594 – Standard for Electric Vehicle Supply Equipment (EVSE); Current Edition, Including All Revisions

#### UL 3141 – Outline of Investigation for Power Control Systems; Current Edition, Including All Revisions

## Submittals – for Review/approval

### The following information shall be submitted to the Engineer:

#### Dimension outline / station elevation drawing

#### Product data sheets

#### Service level and warranty documents

#### Cloud plan documents

#### Certificates (UL, OCPP 2.0.1, CTEP/NTEP, etc.) where applicable

## submittals – for construction

### The following information, if applicable and available, shall be submitted for record purposes:

#### Final as-built drawings and information for items listed in Section 1.2

#### Wiring diagrams and/or installation guide

#### Manufacturer’s site design documentation

## Qualifications

#### The manufacturer of the assembly shall be the manufacturer of the major components within the assembly.

#### The EVCS shall be certified to comply with the applicable codes, industry standards, and applicable federal and state regulations.

#### For the equipment specified herein, the manufacturer shall be ISO 9001 or 9002 certified.

#### The manufacturer of this equipment shall have experience in designing and manufacturing EV charging stations for a minimum period of fifteen (15) years.

## WARRANTY

### Provide a minimum two-year manufacturer warranty covering repair or replacement due to defective materials or workmanship. See PART 2 for Basis of Design warranty and support plans selected.

## Regulatory Requirements

### The ChargePoint charging station shall be NRTL certified to the UL standard.

## Delivery, Storage and Handling

### Equipment shall be handled and stored in accordance with the manufacturer’s instructions.

## operation and maintenance manuals

### Equipment operation and maintenance manuals shall be provided with each kit shipped and shall include instruction leaflets and instruction bulletins for the complete assembly and each major component.

# products

## manufacturers

### Basis of Design (BoD) Manufacturer: ChargePoint; www.chargepoint.com

### Other Acceptable Manufacturers

#### ChargePoint powered by Eaton; www.chargepoint.com; www.eaton.com/chargepoint

#### <<__________>>

### The listing of specific manufacturers above does not imply acceptance of their products that do not meet the specified ratings, features and functions. Manufacturers listed above are not relieved from meeting these specifications in their entirety. Products in compliance with the specification and manufactured by others not named will be considered <<only if pre-approved by the Engineer; or ______>> a minimum of <<ten (10); or _____>> days prior to bid date.

## General requirements

### Hardware and software shall be produced by and obtained from a single manufacturer.

### Selected hardware and software solution must meet: ISO 27001, ISO 9001, PCI DSS, AICPA SOC2, FedRAMP LI-SaaS certifications.

## Electric vehicle charging stations (evcs)

### Ratings

#### cULus Listing to UL2202

#### UL Listing to UL3141

#### Energy Star Certified

#### NTEP Certified

#### Storage temperature: -40˚F to +158˚F (-40˚C to +70˚C)

#### Operating temperature: -40˚F to +131˚F (-40˚C to +55˚C)

#### Operating humidity: Up to 95% at +122˚F (+50˚C) non-condensing

#### Input voltage: <<480Y VAC; 600Y VAC>>, 3-phase, 60 Hz

#### Output voltage: 100 – 1000 VDC

#### Surge protection: 6 kV @ 3,000 A, tested to IEC 6100-4-5

#### Enclosure rating: NEMA Type 3R, IP55

#### Impact rating: IK10

#### Operational altitude: 9,800 ft (3,000m) without derating, 13,123 ft (4,000m) with derating

#### Power factor: 0.99 at full load

#### Power conversion efficiency: Up to 97%

#### Harmonics: iTHD < 5%, complying with IEEE 519

### Models

#### ChargePoint Express Solo

##### EVCS shall be a monolithic solution, meaning one unit that contains power electronics (rectifiers), dispenser, and user interface, within a single cabinet, with the option to add additional dispensers downstream.

##### Connector: ChargePoint Omni PortTM; provides both NACS (SAE J3400) and CCS1 (SAE J1772 Combo) connectors at each charging port.

###### EVCS shall feature locking holsters that only release when an authorized driver authenticates the charging session at the station.

##### Port configuration: <<single port; dual port>>

##### Mounting:

###### EVCS shall be mounted on a concrete pad.

###### EVCS shall come with a concrete mounting template.

Product: Express Solo Concrete Mounting Template

##### Electrical Capabilities

###### Maximum output power: <<600 kW @ 480Y VAC / 625 kW @ 600Y VAC; 400 kW @ 480Y VAC / 450 kW @ 600Y VAC; 200 kW @ 480Y VAC / 225 kW @ 600Y VAC>>

###### Input current rating, see below and project drawings for circuit sizes.

600kW Model: <<769A (1000A breaker) @ 480Y VAC>>

625kW @ 600Y VAC: <<641A (900A breaker)>>

400kW Model: <<515A (700A breaker) @ 480Y VAC>>

450kW @ 600Y VAC: <<463A (600A breaker)>>

200kW Model: <<258A (350A breaker) @ 480Y VAC>>

225kW @ 600Y VAC: <<232A (300A breaker)>>

###### EVCS shall have integrated metering capabilities and be certified per NTEP

##### Charger cord length: <<17 feet; 25 feet>>

###### <<Charger cords shall be cut-resistant, constructed using stainless steel and Kevlar® reinforcement.>>

###### Charger cords shall be <<air-cooled; liquid-cooled>>.

###### EVCS shall have <<integral; external>> cable management.

##### Enclosure shall be NEMA 250, Type 3R.

##### EVCS shall include a <<15 inch; 8 inch>>, full color display with full motion video, UV protection, and multi-language support.

##### EVCS shall support on-station video uploads.

##### EVCS shall have an integral, real-time status indicator light.

##### EVCS shall have hardware capable of bidirectional energy flow.

##### EVCS shall support authentication and payment:

###### RFID: ISO 15693, ISO 14443, NEMA EVSE 1.2-2015

###### Virtual RFID NFC (Tap to Charge)

###### Contactless Credit Card (Tap to Pay)

###### Virtual Contactless Credit Card (Apple Pay, Google Pay)

###### Remote start sessions via mobile app and in-vehicle dash (if supported by vehicle) ISO 15118-2, Plug & Charge ISO 15118-20

##### EVCS shall provide real-time vandalism detection and prevention through visible and audible alarms on both the affected station and nearby stations and provide a method for notifying station operators via text (SMS) and email.

###### Product: ChargePoint Protect

##### EVCS shall seamlessly integrate with the Charge Point Operator (CPO) software.

###### Product: ChargePoint Platform

An annual subscription license is required per charging port, available in one year increments up to five years.

Refer to section 2.3 SOFTWARE for more information about the ChargePoint Platform.

###### EVCS shall support the Open Charge Point Protocol (OCPP) version 2.0.1 for monitoring and control into Charge Point Operator (CPO) software that supports OCPP communications.

##### EVCS shall support over-the-air (OTA) software updates.

##### EVCS shall have a modular architecture, allowing for field-replaceable parts.

##### EVCS shall have the ability to be branded with vinyl inserts and have customizable screen branding options.

##### EVCS shall have the ability to distribute high voltage DC power to downstream dispensers.

###### Product: ChargePoint Power Link 2000

Each downstream dispenser shall not require an external dedicated AC input feed to operate. Input feed requirement shall consist of auxiliary 48VDC, 20A per dispenser unit, fed from the upstream Express Solo unit.

###### Each Express Solo station may be paired with up to (2) additional charging ports, total of (4) ports simultaneously charging and sharing the selected output power.

##### EVCS shall have the ability to pair with another Express Solo station.

###### Max output power (paired): <<750 kW @ 480Y VAC; 500 kW @ 480Y VAC; 250 kW @ 480Y VAC>>

## SOFTWARE

### Charge Point Operator (CPO) Software

#### Product: ChargePoint Platform

#### The software shall support license subscriptions and renewals in one year increments up to five years in length.

#### The software platform shall be capable of supporting both public and fleet project applications, offering different software plans/features for the different project types.

#### The software platform shall:

##### Enable 24/7 access to tools for remote monitoring and real-time status updates of EVCS across multiple installation sites.

##### Provide a user-friendly dashboard to create aggregated reporting and analytics.

##### Grant the site host (owner) administrative controls, including user management tools and the ability to set station access and pricing policies. Pricing policies shall:

###### Be fully customizable to support the owner’s specific needs.

###### Support free charging, tiered pricing, and time of use pricing.

###### Support time-based (per hour charging or per hour plugged in) or energy-based (per kilowatt-hour energy delivered).

###### Support different pricing structures in time increments designated by the site host (owner).

###### Provide a discount structure to allow the site host greater control and flexibility based on their customer profiles.

##### Allow for unlimited number of driver groups for custom pricing, access and other policies based on the driver group

##### Offer, as an option, EV charging station power management capabilities. The power management function shall:

###### Allow balancing of EV charging station energy so that total output stays within an infrastructure’s capacity.

###### Support the following strategies:

Site Level – Facilitates oversubscription of the combined charging ports and stations in aggregate to a site, or transformer

##### Integrate with networked EVCS through annual subscriptions providing the following features at the charging station:

###### Provide optional access to the station’s proprietary API.

###### Enable 24/7 support for both drivers and station owners.

###### Provide Waitlist functionality for virtual queueing of drivers. For more information about Waitlist, refer to the Waitlist FAQ available on the ChargePoint website.

### Driver Mobile Application

#### Selected hardware and software solution must provide a mobile driver application that is free to download and use.

#### Product: ChargePoint mobile application

#### Driver mobile application shall allow drivers to:

##### Find available charging stations

##### Pay for and receive notifications about their charging sessions.

##### Join waitlists.

### Installer Mobile Application

#### Manufacturer of EVCS hardware shall provide a mobile application for station installers.

#### Product: ChargePoint Installer mobile application

#### Installer application shall:

##### Provide access to EVCS installation documentation

##### Provide guided, step-by-step instructions during on-site installation of charging equipment

##### Allow installer to view and clear station faults

## COMMUNICATIONS

### EVCS and the ChargePoint Platform communicate together through ChargePoint Cloud Services via an active internet connection.

### Each EVCS shall have an in-built cellular modem (4G LTE); an external gateway shall not be required for communication with ChargePoint Cloud Services.

#### Contractor to confirm with Engineer that cellular signal strength is strong at EVCS location(s) and meets connectivity guideline specs outlined in Manufacturer’s Site Design Guide document or equivalent.

#### EVCS manufacturer shall provide alternate options for communication with ChargePoint Cloud Services, such as Ethernet and/or Wifi.

## WARRANTY & Support Plans

### Electric Vehicle Supply Equipment hardware and software must provide 24/7/365 driver and station owner support. Support must be provided as a single point of contact for both software-related issues and hardware-related issues.

### Installation of EVCS must be performed by an installer that is certified and/or authorized by EVCS manufacturer.

------ Select one of the below warranty / support plan options ------

### Station shall be purchased with manufacturer’s standard warranty.

#### Product: ChargePoint standard, 2-year, parts only warranty

#### Standard warranty shall include:

##### Parts cost coverage for issues covered by warranty

##### Shipping of parts to customers

### Station shall be purchased with Parts and Labor warranty program.

#### Product: ChargePoint Assure

##### One annual license required per charging station.

##### Installation of EVCS must be performed by an installer that is ChargePoint DC Certified with the installation microcredential for the EVCS product being installed from ChargePoint University.

#### Parts and labor warranty program shall include:

##### Parts cost coverage for issues covered by warranty

##### Delivery of parts to certified service partner

##### Certified technician dispatched for on-site repair once parts are received

##### Labor cost coverage, including labor for issues not covered by warranty such as vandalism and accidents

##### Proactive monitoring and diagnostics

##### Unlimited remote configuration changes and optimization support

#### The parts and labor warranty program shall support subscriptions and renewals in one year increments up to five years in length.

# execution

## installation

### The equipment shall be installed in accordance with manufacturer’s recommendations by a ChargePoint DC Certified entity with the necessary installation microcredential from ChargePoint University.

### The equipment shall conform to all NEC and local codes.

### The equipment shall be activated by a ChargePoint Deployment Specialist.

#### Product: CP-ACTIVATION; one activation service required per charging station.

##### Station Activation cannot be completed without qualified credentials from the installer.

###### Installer must be ChargePoint DC Certified and must be qualified to install the ChargePoint station model specified through ChargePoint University (https://www.chargepoint.com/partners/training-certification).

##### Installer must provide the manufacturer with contact information for the individual responsible for management of the EVCS (facility manager or other). The station Activation process and the appropriate onboarding and software setup cannot be completed without an appropriate contact being identified.

## EXAMINATION

### Verify that ratings of the electric vehicle supply equipment (EVSE) are consistent with indicated requirements

### Confirm network connectivity meets manufacturer’s minimum requirements

### Verify proper mounting and installation of EVSE per manufacturer’s installation guide

### Verify that EVSE and accessories are free from obstructions and meet manufacturer’s minimum clearance requirements

### Verify that mounting surfaces are ready to receive EVSE and conform to manufacturer’s specifications or have been verified by an authorized consultant.

### Verify that branch circuit wiring installation is completed, tested, and ready for connection to the charging units.

### Verify that conditions are satisfactory for installation prior to starting work

## COMMISSIONING

### EVCS must be commissioned by a ChargePoint Authorized Commissioning Partner (ACP) prior to station Activation. ACP must be ChargePoint DC Certified with the necessary commissioning microcredential from ChargePoint University.

### Prepare and start system in accordance with manufacturer’s instructions.

### Program system parameters according to requirements of owner.

### Test system for proper operation.

### Correct defective work, adjust for proper operation and retest until entire system complies with Contract Documents.

### Submit detailed reports indicating inspection and testing results and corrective actions taken.